GUIDEFORM SPECIFICATIONS, DISTRIBUTION PANEL BOARD

PART 1.	GENERAL REQUIREMENTS

- SCOPE

This specification describes the requirements of a 1-input, 2-panel, Shared Parallel (SP), 42-circuit, Wall-mounted panel board designed to supply power to critical and sensitive loads. It includes all equipment to interface and monitor the AC power source to the intended load.

- RELATED DOCUMENTS

The manufacturer must supply equipment in compliance with any plans or drawings supplied by the engineer in addition to this specification.  The manufacturer must note any deviations to these plans or drawings or to this specification.

- DEFINITIONS/STANDARDS

  - The specified panel board shall be designed, manufactured, tested, and installed in compliance with:

    - American National Standards Institute (ANSI)

    - Underwriters Laboratories (UL)

    - Institute of Electrical and Electronics Engineers (IEEE)

    - National Electrical Code -latest edition (NFPA 70)

    - National Electrical Manufacturers Association (NEMA)

    - Canadian Standards Association (CSA)

  - The unit shall be listed to UL 67 by a Nationally Recognized Testing Laboratory (NRTL).

- SUBMITTALS

  - Submittals shall be made in accordance with specified procedures including, but not limited to:

    - A compliance review of all specifications and associated material.  The review will be paragraph by paragraph designating specification Compliance with a “C”, Deviation with a “D”, or Exception with an “E”.  The reason for each proposed Deviation and Exception shall be given along with the intent of how the specification shall be satisfied.

    - Mechanical drawings showing dimensions, footprints, wiring entrance locations and clearances for proposed equipment.

    - An electrical one-line drawing of the equipment configuration.

    - Manufacturer’s datasheet for main circuit breakers.

    - Manufacturer’s datasheet for branch circuit breakers.

    - Upon shipment the manufacturer shall furnish an Equipment Manual detailing the installation, start-up, operation and maintenance instructions for the panel board.

    - A recommended list of spare parts shall be supplied upon customer’s request.

- WARRANTY

The manufacturer shall provide a warranty against defects in material and workmanship for 12 months after initial start-up or 18 months after ship date, whichever occurs first.  During the first 12 months of operation, there shall be no cost to the owner for any corrective repairs.

- QUALITY ASSURANCE

The specified system shall be factory-tested before shipment. Testing shall include, but shall not be limited to: Quality Control Checks, “Hi-Pot” Test (two times rated voltage plus 1000 volts, per UL requirements). The system shall be designed and manufactured according to world-class quality standards.  Compliance with ISO-9002 Quality Assurance requirements shall be observed.

PART 2	PRODUCT

- DESCRIPTION

The panel board shall have (1) main input feeder, designated as Feeder 1. Feeder 1 shall be internally connected to (1) main automatic (Thermal Magnetic Trip) circuit breaker, designated as Main CB1. The output of Main CB1 shall connect to (2) 42-circuit panel boards, designated as Panel Board 1 and Panel Board 2.

- RATINGS

  - Electrical

    - Input and Output voltage shall be 120/208V, 3-Phase, 4-Wire + Ground, and 60Hz.

    - Panel board is rated for operation in power circuits with perspective symmetrical current no greater than 25kA.

    - Panel board automatic (Thermal Magnetic Trip) circuit breaker shall be 400 continuous duty rated; Plug-in; 65kAIC @ 240VAC (per UL ratings).

    - Panel board shall be 225A continuous duty rated; with a 25kA withstand rating.

    - All neutral terminals shall be rated.

    - Each Panel board shall have the ability to house up to 42 circuits, of 10-60A rating. Each panel board shall have the ability to house up to four (4), 100A, 3-pole branch circuit breakers.

    - Branch circuit breakers shall be plug-in.

    - Branch circuit breakers shall have an interrupting rating of 25kAIC @ 208VAC in series with the main.

  - Environmental

    - Storage temperature range shall be -55 to +75°C (-67 to +185°F).

    - Operating temperature range shall be 0 to 40°C (+32 to 104°F).

    - Non-condensing relative humidity range 0% to 95%.

    - Audible noise shall not exceed 45dBA at 5 ft. (1.5m) from the surface of the panel board.

- COMPONENTS

  - Frame Construction and Enclosure

    - The enclosure shall be free-standing, NEMA-1. The frame shall be constructed of 16-gauge welded or formed steel to provide a strong substructure. A hinged front door shall be equipped with a key-lock and shall have a viewport that allows the operator to view the position of the main and branch circuit breakers.  The color of the exterior panels shall be the manufacturer’s standard color (RAL 9005 or equal).

    - The panel board shall be a door-in-door style construction. It shall have two separate dead front doors: one hinged dead front door shall protect the operator from exposure to the 42-circuit section; the second hinged dead front door shall protect the operator from exposure to the incoming feeder terminations and the line side of the main circuit breaker.

    - The panel board shall be designed for top cable entry of main circuits and branch circuits.

      - Knock outs for main circuit feeder cable shall be provided

      - Knock outs for branch circuit output cables shall be provided

    - Input source terminals (3 phases + neutral + ground) shall be able to accommodate long-barreled, Two-hole Compression Lug Terminals from incoming feeder cables. Input terminals with mechanical type (set screw) lugs are not acceptable. Lugs shall be provided by the installation contractor.

    - It shall be possible to thermal scan all internal bolted connections from the front or top of the panel board. A porthole shall be provided for the thermal scanning of the input cable phase terminations.

    - Gutters on either side of the panel board chassis shall be equipped with wire ways to allow for secured and planned routing of load cables.

    - Panel board dimensions shall not exceed W x D x H. Front clearance of 36” shall be required. Side clearances of 1” on either side of the panel board shall be required for adequate venting.

  - Circuit Breakers

    - Panel board mains shall have the following attribute values:

      - Frame Rating:  400

      - Trip Rating:  225

      - Circuit Breaker Type:  Thermal Magnetic Trip

      - Mounting Type:  Plug-in

      - Number of Poles:  3

  - Panel boards

    - The distribution panel board shall be equipped with (2), 42-pole, 225A, 3-phase panel board chassis with a minimum withstand rating of 25kA.

    - The panel board chassis shall be able to accommodate a minimum of four (4), 100AF, 3-pole branch circuit breakers. All other circuit positions shall be able to accept circuit breakers rated 10 – 60A.

    - The panel board chassis shall have 42 neutral lugs; and 42 ground lugs integral to its design.

    - The panel board chassis shall be IP-20 finger-safe rated.

  - Branch Circuit Breakers

    - Branch circuit breakers shall be plug-in and rated for 25kA in series with the main. However, a means of bolting the plug in breaker to the panel board shall be provided. The securing bolt shall be isolated and not come in contact with energized, live parts.

    - The branch circuit breaker shall be current-limiting with the property that in the event of a downstream bolted fault, the circuit breaker shall trip open in less than 4 milliseconds. This will ensure that the panel board’s main bus voltage remains within the voltage tolerance of information technology equipment as defined by the ITIC power quality curve.

    - The branch circuit breakers shall be available in 1-pole, 2-pole and 3-pole variants from 2A up to 100A.

    - Branch circuit breakers shall be selective trip coordinated with the main circuit breaker for the system ratings.

  - Main Circuit Monitor

    - The panel board monitor shall provide the following metering information for the main panel board bus:

      - Panel board voltage: 3-phase, L-L or L-N, RMS

      - Panel board phase rotation

      - Voltage THD

    - The panel board monitor shall record waveforms of critical power quality events at the panel board main bus. Each waveform shall record the three phase voltage signal at the panel board main bus 6 cycles before and 6 cycles after the power quality event. A power quality event at the panel board main bus is defined as:

      - Under voltage (UV) caused by a sag

      - Over voltage (OV) caused by a swell

    - The panel board monitor shall store up to 10 waveforms in non-volatile memory. The waveforms shall be available in a common graphical format (.gif, .jpg, etc.)

  - Remote Communications

    - Each panel board monitor shall be capable of communicating remotely either over Ethernet (single CAT5 cable to the panel board monitor). Each panel board shall be assigned a unique IP address on the facility LAN.

    - Meters and Alarms shall be available via Modbus TCP. The manufacturer shall provide the Modbus register list.

    - Alarms shall be available via SNMP.

    - Waveforms, Meters, Alarms, and uploading of circuit names and setpoints shall be available via http:// web browser

    - Uploading of circuit names and setpoints shall be available via Bluetooth.

PART 3	EXECUTION

- FACTORY TESTING

  - Each panel board shall be Hi-Pot tested per UL requirements

  - Each panel board monitor shall be tested for functionality. Panel board monitor circuit boards shall be serialized. A test report of each individual panel board monitor circuit board shall be made available upon request.

- COMMISSIONING

  - After installation, provide a qualified, experienced manufacturer authorized representative to supervise and assist in the commissioning of the panel board monitor.